It's a Siemens SSY319 — a 3-position electric valve actuator, 230V AC, 300N force, 150s travel time.

Key specs visible on your label match perfectly:

- AC 230V +15%

- 50/60Hz, 6VA

- 5...50°C, IP40

Y1 / Y2 (visible on the label) are the two 3-position control terminals:

- Y1 → drives valve in one direction (open)

- Y2 → drives valve in the other direction (close)

- Both off → valve stops and holds position

This confirms your relay wiring in the code is correct — PIN_RELAY_VALVE_CW (GPIO 11) for Y1 and PIN_RELAY_VALVE_CCW (GPIO 12) for Y2.